**HIGH-SPEED ROLL-**UP DOOR, type "EFA-SRT®-S"

Manufacture, delivery and installation of:

High-speed roll-up door type "EFA-SRT®-S", with electro-mechanical high-performance door drive for continuous industrial use

To balance the weight of the door leaf and to open the door manually in the event of a power failure (according to DIN EN 12604), a special tension spring mechanism must be integrated into the side door frames. This durable and extremely maintenance-friendly counter-traction device is mandatory. Constructions with torsion springs are not permitted; Standard door leaf made of 3 mm thick PVC, fully transparent, guided on the side and wound onto a horizontally mounted shaft; PVC door leaves generally with vertical warning strips. A maintenance-free door leaf tensioner is to be provided in order to keep the door leaf permanently under tension when closing. In addition, the lateral CURTAIN GUIDES are to be designed with special guide devices in such a way that problem-free winding and unwinding is guaranteed even under wind loads. All-round sealed steel frame construction sendzimir-galvanised as standard.

The DOOR DRIVE is carried out by means of a geared brake motor, which is to be designed as a high-frequency motor. The door positions are permanently recorded using non-wearing, inductive proximity switches, with the end positions being determined electronically. Electromechanical limit switches are not permitted for this.

**OPENING SPEED: Up to approx. 1.0 m/sec.**

**Max. DOOR LEAF SPEED: Up to approx. 1.5 m/sec.**

(depending on door size)

**CLOSING SPEED: Up to approx. 0.6 m/sec.**

The **MICROPROCESSOR CONTROL** is installed together with the integrated frequency converter in a separate plastic switch cabinet, protection class IP 65. Connection to electricity 230V/ 50 Hz on site.

The scope of delivery includes an electrical safety contact edge according to DIN EN12453, self-monitoring: the supply cable must be routed in a protected energy chain within the door frame.

Regulations according to DIN EN 13241-1 are fulfilled;

for clear opening dimensions

Width = ............... mm x Height = ............... mm

**Manufacturer Proof:**

EFAFLEX Tor- und Sicherheitsysteme GmbH & Co. KG

[www.efaflex.com](http://www.efaflex.com)

**OPTIONS for High-Speed Roll-Up Door "EFA-SRT®-S"**

Increasing the door leaf speed:

**OPENING SPEED: Up to approx. 1.5 m/sec.**

**Max. DOOR LEAF SPEED: Up to approx. 2.0 m/sec.**

(depending on door size)

**CLOSING SPEED: Up to approx. 0.75 m/sec.**

**Cover of the winding shaft/ motor:**

Engine cover

Front cover over motor and shaft

Complete cover of motor and shaft

**Surface:**

Powder coating of all galvanised steel parts in a colour according to RAL \_\_\_\_\_\_\_\_\_\_ (metallic colours are not available)

**Special Curtains:**

Polyester fabric 2.0 mm thick, laterally stable, FDA approved

red / orange / yellow: not antistatic, silicone-free

blue / grey-white: antistatic, silicone-free,

**as before, however**

with sight strips made of fully transparent PVC

(in the case of a door curtain with a viewing window, only partially antistatic and partially

approved for food industry)

**Alternatively:**

Polyester fabric 2.0 mm thick, black-grey, laterally stable, urethane-impregnated,

Flame retardant B1 (SE) according to DIN EN 20340 antistatic, silicone-free